Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by AVITRU, LLC for the AIA

SECTION 221316 - SANITARY WASTE AND VENT PIPING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to revise this Section.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Hub-and-spigot, cast-iron soil pipe and fittings.

          - Hubless, cast-iron soil pipe and fittings.

          - Galvanized-steel pipe and fittings.

          - Stainless-steel drainage pipe and fittings.

          - Ductile-iron pipe and fittings.

          - Copper tube and fittings.

          - PVC pipe and fittings.

          - Encasement for underground metal piping.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 221313 "Facility Sanitary Sewers" for sanitary sewerage piping and structures outside the building.

          - Section 221329 "Sanitary Sewerage Pumps" for effluent and sewage pumps.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

        - Sustainable Design Submittals:

          - <Double click to insert sustainable design text for adhesives.>

Retain "Shop Drawings" Paragraph below if retaining a hubless, single-stack drainage system.

        - Shop Drawings: Include plans, elevations, sections, and details.

      - INFORMATIONAL SUBMITTALS

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying mechanical vibration, supports, and seismic controls. See ASCE/SEI 7 for certification requirements for equipment and components.

        - Seismic Qualification Certificates: For waste and vent piping, accessories, and components, from manufacturer.

          - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - Detailed description of piping anchorage devices on which the certification is based and their installation requirements.

        - Field quality-control reports.

      - FIELD CONDITIONS

Retain paragraph below if interruption of existing sanitary waste service is required.

        - Interruption of Existing Sanitary Waste Service: Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

          - Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of sanitary waste service.

          - Do not proceed with interruption of sanitary waste service without [Architect's] [Construction Manager's] [Owner's] written permission.

      - WARRANTY

        - Listed manufacturers to provide labeling and warranty of their respective products.

- PRODUCTS

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or Avitru. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Components and installation shall be capable of withstanding the following minimum working pressure unless otherwise indicated:

Revise pressure ratings in two subparagraphs below to suit Project. Coordinate with Section 221319 "Sanitary Waste Piping Specialties." Soil and waste piping may require higher rating if used in high-rise buildings.

          - Soil, Waste, and Vent Piping: 10-foot head of water.

          - Waste, Force-Main Piping: 50 psig.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for Projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer. Verify requirements of authorities having jurisdiction.

        - Seismic Performance: Soil, waste, and vent piping and support and installation shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

      - PIPING MATERIALS

        - All cast iron soil pipe and fittings shall be marked with the collective trademark of the Cast Iron Soil Pipe Institute (CISPI) ® and listed by NSF International.

See piping materials articles in the Evaluations for a discussion of piping materials covered by referenced standards.

        - Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, fitting materials, and joining methods for specific services, service locations, and pipe sizes.

      - HUB-AND-SPIGOT, CAST-IRON SOIL PIPE AND FITTINGS ([Above] [Below] Grade)

Pipe and fittings in this article are available in NPS 2 to NPS 15 (DN 50 to DN 375).

        - Pipe and Fittings: ASTM A 74, [Service] [Extra Heavy] class.

        - Gaskets: ASTM C 564, rubber.

        - Caulking Materials: ASTM B 29, pure lead and oakum or hemp fiber.

        - Tensile Strength: 21,000 psig minimum.

        - Pipe and fittings shall be marked with the collective trademark of the Cast Iron Soil Pipe Institute ® and listed by NSF International.

        - Each length of pipe and each fitting shall be plainly marked with size, country of origin, and name of manufacturer, or manufacturer’s registered trademark by which the manufacturer can be readily identified after installation.

      - HUBLESS, CAST-IRON SOIL PIPE AND FITTINGS ([Above] [Below] Grade)

        - Pipe and Fittings: ASTM A 888 and CISPI 301.

Retain "Single-Stack Aerator Fittings" Paragraph below only if Project has a hubless, single-stack drainage system. Fittings below are available in NPS 2 to NPS 8 (DN 50 to DN 200). Use of hubless, single-stack aerator fittings does not eliminate need for standard hubless, cast-iron pipe fittings.

        - Tensile Strength: 21,000 psig minimum.

        - Pipe and fittings shall be marked with the collective trademark of the Cast Iron Soil Pipe Institute ® and listed by NSF International.

        - Each length of pipe and each fitting shall be plainly marked with size, country of origin, and name of manufacturer, or manufacturer’s registered trademark by which the manufacturer can be readily identified after installation.

Retain one or more of three hubless fittings paragraphs below. If retaining more than one, indicate location of each type on Drawings. Couplings in "CISPI, Hubless-Piping Couplings" Paragraph below are economical and are made in NPS 1-1/2 to NPS 15 (DN 40 to DN 375). They may be unsuitable for installation in corrosive soil.

        - CISPI, Hubless-Piping Couplings:

          - Manufacturers: Subject to compliance with requirements. Provide products by one of the following:

- a. Ideal Tridon

- b. ANACO-Husky

- c. Tyler Couplings

- d. Mission Rubber Company

          - Standards: ASTM C 1277 and CISPI 310.

          - Description: Shield Assemblies shall consist of stainless-steel bi-directional corrugated shield with stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve with integral, center pipe stop. Couplings shall bear the trademark NSF International.

Couplings in "Heavy-Duty, Hubless-Piping Couplings" Paragraph below are made in NPS 1-1/2 to NPS 15 (DN 40 to DN 375).

        - Heavy-Duty, Hubless-Piping Couplings:

          - Manufacturers: Subject to compliance with requirements. Provide products by one of the following:

- a. Ideal Tridon

- b. ANACO-Husky

- c. Tyler Couplings

- d. Mission Rubber Company

          - Standards: ASTM C 1540.

          - Description: Shield Assemblies shall consist of stainless-steel bi-directional corrugated shield with stainless-steel bands and tightening devices; and ASTM C 564, rubber sleeve with integral, center pipe stop.

      - HIGH PERFORMANCE COATED HUB-AND-SPIGOT, CAST-IRON SOIL PIPE AND FITTINGS ([Above] [Below] Grade)

Pipe and fittings in this article are available in NPS 2 to NPS 15 (DN 50 to DN 375).

        - Pipe and Fittings: ASTM A 74, Service class.

        - Gaskets: ASTM C 564, rubber.

        - Caulking Materials: ASTM B 29, pure lead and oakum or hemp fiber.

        - Tensile Strength: 21,000 psig minimum.

        - All cast iron soil pipe and fittings shall be marked with the collective trademark of the Cast Iron Soil Pipe Institute (CISPI) and listed by NSF International.

        - Each length of pipe and each fitting shall be plainly marked with size, country of origin, and name of manufacturer, or manufacturer’s registered trademark by which the manufacturer can be readily identified after installation.

        - The inside of each pipe shall be reamed prior to coating to decrease the coefficient of friction.

        - Pipe Coating on both ID and OD: Chemically deposited zinc-phosphate pretreatment layer followed by an electrically deposited, high performance cathodic epoxy coating, and finally an electrically deposited, high performance anodic epoxy topcoat.  Coating thickness shall be 5 mils or greater on both the OD and ID.

        - Fitting Coating on both ID and OD: Chemically deposited zinc-phosphate pretreatment layer followed by an electrically deposited, high performance cathodic epoxy coating, and finally an epoxy acrylic powder topcoat. Coating thickness shall be 5 mils or greater on both the OD and ID.

        - Coating Performance:  Pipe and Fitting Coatings must pass the following performance specifications per EN 877:

- a. 350 hours of salt spray testing

- b. Resistance to wastewater for 30 days at 73⁰ F

- c. Chemical resistance from pH 2 to pH 12 for 30 days at 73⁰ F

- d. Resistance to hot water for 24 hours at 203⁰ F

      - HIGH PERFORMANCE COATED HUBLESS, CAST-IRON SOIL PIPE AND FITTINGS ([Above] [Below] Grade)

        - Pipe and Fittings: ASTM A 888 or CISPI 301.

Retain "Single-Stack Aerator Fittings" Paragraph below only if Project has a hubless, single-stack drainage system. Fittings below are available in NPS 2 to NPS 8 (DN 50 to DN 200). Use of hubless, single-stack aerator fittings does not eliminate need for standard hubless, cast-iron pipe fittings.

        - Tensile Strength: 21,000 psig minimum.

        - All cast iron soil pipe and fittings shall be marked with the collective trademark of the Cast Iron Soil Pipe Institute (CISPI) and listed by NSF International.

        - Each length of pipe and each fitting shall be plainly marked with size, country of origin, and name of manufacturer, or manufacturer’s registered trademark by which the manufacturer can be readily identified after installation.

        - The inside of each pipe shall be reamed prior to coating to decrease the coefficient of friction.

        - Pipe Coating on both ID and OD: Chemically deposited zinc-phosphate pretreatment layer followed by an electrically deposited, high performance cathodic epoxy coating, and finally an electrically deposited, high performance anodic epoxy topcoat.  Coating thickness shall be 5 mils or greater on both the OD and ID.

        - Fitting Coating on both ID and OD: Chemically deposited zinc-phosphate pretreatment layer followed by an electrically deposited, high performance cathodic epoxy coating, and finally an epoxy acrylic powder topcoat.  Coating thickness shall be 5 mils or greater on both the OD and ID.

        - Coating Performance:  Pipe and Fitting Coatings must pass the following performance specifications per EN 877:

- a. 350 hours of salt spray testing

- b. Resistance to wastewater for 30 days at 73⁰ F

- c. Chemical resistance from pH 2 to pH 12 for 30 days at 73⁰ F

- d. Resistance to hot water for 24 hours at 203⁰ F

Couplings in "Cast-Iron, Hubless-Piping Couplings" Paragraph below are made in NPS 1-1/2 to NPS 10 (DN 40 to DN 250).

      - GALVANIZED-STEEL PIPE AND FITTINGS

Pipe in "Galvanized-Steel Pipe" Paragraph below is available in NPS 1/8 to NPS 26 (DN 6 to DN 650).

        - Galvanized-Steel Pipe: ASTM A 53/A 53M, Type E, Standard Weight class. Include square-cut-grooved or threaded ends matching joining method.

Fittings in "(Galvanized-)Cast-Iron Drainage Fittings" Paragraph below are available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200).

        - [Galvanized-]Cast-Iron Drainage Fittings: ASME B16.12, threaded.

        - Steel Pipe Pressure Fittings:

Fittings in "(Galvanized-)Steel Pipe Nipples" Subparagraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

          - [Galvanized-]Steel Pipe Nipples: ASTM A 733, made of ASTM A 53/A 53M or ASTM A 106/A 106M, Schedule 40, seamless steel pipe. Include ends matching joining method.

Fittings in "Malleable-Iron Unions" Subparagraph below are available in NPS 1/8 to NPS 4 (DN 6 to DN 100).

          - Malleable-Iron Unions: ASME B16.39; Class 150; hexagonal-stock body with ball-and-socket, metal-to-metal, bronze seating surface; and female threaded ends.

Fittings in "(Galvanized-)Gray-Iron, Threaded Fittings" Subparagraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

          - [Galvanized-]Gray-Iron, Threaded Fittings: ASME B16.4, Class 125, standard pattern.

Flanges in "Cast-Iron Flanges" Paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

        - Cast-Iron Flanges: ASME B16.1, Class 125.

          - Flange Gasket Materials: ASME B16.21, full-face, flat, nonmetallic, asbestos-free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

          - Flange Bolts and Nuts: ASME B18.2.1, carbon steel unless otherwise indicated.

Fittings and couplings in "Grooved-Joint, Galvanized-Steel-Pipe Appurtenances" Paragraph below are available in NPS 3/4 to NPS 24 (DN 20 to DN 600).

        - Grooved-Joint, Galvanized-Steel-Pipe Appurtenances:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Galvanized, Grooved-End Fittings for Galvanized-Steel Piping: ASTM A 536 ductile-iron castings, ASTM A 47/A 47M malleable-iron castings, ASTM A 234/A 234M forged steel fittings, or ASTM A 106/A 106M steel pipes with dimensions matching ASTM A 53/A 53M steel pipe, and complying with AWWA C606 for grooved ends.

Couplings in "Grooved Mechanical Couplings for Galvanized-Steel Piping" Subparagraph below are available in at least NPS 3/4 to NPS 24 (DN 20 to DN 600).

          - Grooved Mechanical Couplings for Galvanized-Steel Piping: ASTM F 1476, Type I. Include ferrous housing sections with continuous curved keys; EPDM-rubber gasket suitable for hot and cold water; and bolts and nuts.

      - STAINLESS-STEEL DRAINAGE PIPE AND FITTINGS

Pipe and fittings in this article are available in NPS 2 to NPS 8 (DN 50 to DN 200) and are specific to drainage applications.

        - <Double click here to find, evaluate, and insert list of manufacturers and products.>

        - Description: Comply with requirements of ASME A112.3.1, drainage pattern.

        - Material: [Type 304 stainless steel] [Type 316L stainless steel] [Type 304 or 316L stainless steel].

        - Pipe Construction: Seamless.

Retain "Internal Sealing Ring" Article below for elastomeric O-ring sealing materials. Sealing ring materials are permitted for various drain applications. ASME 112.3.1 requires marking or color coding.

        - Internal Sealing Rings: [EPDM] [NBR] <Insert material>[, marked or color coded for the application].

        - Joints: Single or double, socket and spigot ends.

      - DUCTILE-IRON PIPE AND FITTINGS

Retain one of first three paragraphs below. Piping in "Ductile-Iron, Mechanical-Joint Piping" Paragraph is available in NPS 3 to at least NPS 24 (DN 80 to at least DN 600).

        - Ductile-Iron, Mechanical-Joint Piping:

          - Ductile-Iron Pipe: AWWA C151/A21.51, with mechanical-joint bell and plain spigot ends unless grooved or flanged ends are indicated.

          - Ductile-Iron Fittings: AWWA C110/A21.10, mechanical-joint, ductile- or gray-iron standard pattern or AWWA C153/A21.53, ductile-iron compact pattern.

          - Glands, Gaskets, and Bolts: AWWA C111/A21.11, ductile- or gray-iron glands, rubber gaskets, and steel bolts.

Piping in "Ductile-Iron, Push-on-Joint Piping" Paragraph below is available in NPS 3 to NPS 64 (DN 80 to DN 1600).

        - Ductile-Iron, Push-on-Joint Piping:

          - Ductile-Iron Pipe: AWWA C151/A21.51, with push-on-joint bell and plain spigot ends unless grooved or flanged ends are indicated.

          - Ductile-Iron Fittings: AWWA C110/A21.10, push-on-joint, ductile- or gray-iron standard pattern or AWWA C153/A21.53, ductile-iron compact pattern.

          - Gaskets: AWWA C111/A21.11, rubber.

Pipe in "Ductile-Iron, Grooved-Joint Piping" Paragraph below is available in NPS 3 to NPS 64 (DN 80 to DN 1600).

        - Ductile-Iron, Grooved-Joint Piping: AWWA C151/A21.51, with round-cut-grooved ends according to AWWA C606.

Appurtenances in "Ductile-Iron, Grooved-End Pipe Appurtenances" Paragraph below are available in NPS 4 to NPS 24 (DN 100 to DN 600).

        - Ductile-Iron, Grooved-End Pipe Appurtenances:

          - <Double click here to find, evaluate, and insert list of manufacturers and products.>

          - Grooved-End, Ductile-Iron Fittings: ASTM A 536 ductile-iron castings, with dimensions matching AWWA C110/A 21.10 ductile-iron pipe or AWWA C153/A 21.53 ductile-iron fittings, and complying with AWWA C606 for grooved ends.

Couplings in "Grooved Mechanical Couplings for Ductile-Iron Pipe" Subparagraph below are available in NPS 4 to NPS 24 (DN 100 to DN 600). Other AWWA pipe size couplings in NPS 3 to NPS 36 (DN 80 to DN 900) are also available.

          - Grooved Mechanical Couplings for Ductile-Iron Pipe: ASTM F 1476, Type I. Include ferrous housing sections with continuous curved keys; EPDM-rubber center-leg gasket suitable for hot and cold water; and bolts and nuts.

      - COPPER TUBE AND FITTINGS

Tube and fittings in first two paragraphs below are available in NPS 1-1/4 to NPS 8 (DN 32 to DN 200).

        - Copper Type DWV Tube: ASTM B 306, drainage tube, drawn temper.

        - Copper Drainage Fittings: ASME B16.23, cast copper or ASME B16.29, wrought copper, solder-joint fittings.

Tube and fittings in first three paragraphs below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

        - Hard Copper Tube: ASTM B 88, Type L and Type M (ASTM B 88M, Type B and Type C), water tube, drawn temper.

        - Soft Copper Tube: ASTM B 88, Type L (ASTM B 88M, Type B), water tube, annealed temper.

        - Copper Pressure Fittings:

          - Copper Fittings: ASME B16.18, cast-copper-alloy or ASME B16.22, wrought-copper, solder-joint fittings. Furnish wrought-copper fittings if indicated.

Unions in "Copper Unions" Subparagraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

          - Copper Unions: MSS SP-123, copper-alloy, hexagonal-stock body with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

Flanges in "Copper Flanges" Paragraph below are available in NPS 1/4 to at least NPS 6 (DN 8 to at least DN 150).

        - Copper Flanges: ASME B16.24, Class 150, cast copper with solder-joint end.

          - Flange Gasket Materials: ASME B16.21, full-face, flat, nonmetallic, asbestos-free, 1/8-inch (3.2-mm) maximum thickness unless thickness or specific material is indicated.

          - Flange Bolts and Nuts: ASME B18.2.1, carbon steel unless otherwise indicated.

        - Solder: ASTM B 32, lead free with ASTM B 813, water-flushable flux.

      - PVC PIPE AND FITTINGS

Retain first paragraph below if NSF markings are required.

        - Comply with NSF 14, "Plastics Piping Systems Components and Related Materials," for plastic piping components. Include marking with "NSF-dwv" for plastic drain, waste, and vent piping and "NSF-sewer" for plastic sewer piping.

Pipe and fittings in first two paragraphs below are available in NPS 1-1/4 to NPS 12 (DN 32 to DN 300). Retain one or both paragraphs and coordinate with "Piping Schedule" Article.

        - Solid-Wall PVC Pipe: ASTM D 2665, drain, waste, and vent.

        - Cellular-Core PVC Pipe: ASTM F 891, Schedule 40 will not be accepted.

        - PVC Socket Fittings: ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns.

        - PVC Pressure Fittings: ASTM D 2466, Socket Type

        - Primer: ASTM F 656.

          - Primer shall have a VOC content of 550g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24)

          - Adhesive primer shall comply with the testing and product requirements of the California Department of Health Services “Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers”

        - Solvent Cement: ASTM D 2564.

          - PVC solvent cement shall have a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24)

          - Solvent cement shall comply with the testing and product requirements of the California Department of Health Services “Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers”

- 2.12            SPECIALTY PIPE FITTINGS

        - Transition Couplings:

Retain pipe couplings in subparagraphs below if dissimilar piping materials or piping with small differences in OD must be joined.

          - Fitting-Type Transition Couplings: Manufactured piping coupling or specified piping system fitting.

Couplings in "Unshielded, Nonpressure Transition Couplings" Subparagraph below are for underground nonpressure piping and should be available in all sizes.

          - Unshielded, Nonpressure Transition Couplings:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASTM C 1173.

            - Description: Elastomeric, sleeve-type, reducing or transition pattern. Include shear ring and corrosion-resistant-metal tension band and tightening mechanism on each end.

            - End Connections: Same size as and compatible with pipes to be joined.

            - Sleeve Materials:

              - For Cast-Iron Soil Pipes: ASTM C 564, rubber.

              - For Plastic Pipes: ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

              - For Dissimilar Pipes: ASTM D 5926, PVC or other material compatible with pipe materials being joined.

Couplings in "Shielded, Nonpressure Transition Couplings" Subparagraph below are for aboveground nonpressure piping and should be available in most sizes.

          - Shielded, Nonpressure Transition Couplings:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: ASTM C 1460.

            - Description: Elastomeric or rubber sleeve with full-length, corrosion-resistant outer shield and corrosion-resistant-metal tension band and tightening mechanism on each end.

            - End Connections: Same size as and compatible with pipes to be joined.

Couplings in "Pressure Transition Couplings" Subparagraph below are for underground pressure piping and are available in at least NPS 1-1/2 to NPS 24 (DN 40 to DN 600).

          - Pressure Transition Couplings:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Standard: AWWA C219.

            - Description: Metal, sleeve-type same size as, with pressure rating at least equal to, and ends compatible with, pipes to be joined.

            - Center-Sleeve Material: [Manufacturer's standard] [Carbon steel] [Stainless steel] [Ductile iron] [Malleable iron].

            - Gasket Material: Natural or synthetic rubber.

            - Metal Component Finish: Corrosion-resistant coating or material.

        - Dielectric Fittings:

Unions in "Dielectric Unions" Subparagraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

          - Dielectric Unions:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Description:

              - Standard: ASSE 1079.

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

              - Pressure Rating: [125 psig (860 kPa) minimum at 180 deg F (82 deg C)] [150 psig (1035 kPa)] [250 psig (1725 kPa)] <Insert pressure>.

              - End Connections: Solder-joint copper alloy and threaded ferrous.

Flanges in "Dielectric Flanges" Subparagraph below are available in at least NPS 1-1/2 to NPS 4 (DN 40 to DN 100).

          - Dielectric Flanges:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Description:

              - Standard: ASSE 1079.

              - Factory-fabricated, bolted, companion-flange assembly.

Revise pressure rating in first subparagraph below to suit Project, or insert other options for specific applications.

              - Pressure Rating: [125 psig (860 kPa) minimum at 180 deg F (82 deg C)] [150 psig (1035 kPa)] [175 psig (1200 kPa)] [300 psig (2070 kPa)] <Insert pressure>.

              - End Connections: Solder-joint copper alloy and threaded ferrous; threaded solder-joint copper alloy and threaded ferrous.

Flanges in "Dielectric-Flange Insulating Kits" Subparagraph below are available in at least NPS 1/2 to NPS 48 (DN 15 to DN 1200).

          - Dielectric-Flange Insulating Kits:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Description:

              - Nonconducting materials for field assembly of companion flanges.

Revise pressure rating in first subparagraph below to suit Project, or insert other options for specific applications.

              - Pressure Rating: [150 psig (1035 kPa)] <Insert pressure>.

              - Gasket: Neoprene or phenolic.

              - Bolt Sleeves: Phenolic or polyethylene.

              - Washers: Phenolic with steel backing washers.

Nipples in "Dielectric Nipples" Subparagraph below are available in at least NPS 1/2 to NPS 4 (DN 15 to DN 100).

          - Dielectric Nipples:

            - <Double click here to find, evaluate, and insert list of manufacturers and products.>

            - Description:

              - Standard: IAPMO PS 66.

              - Electroplated steel nipple.

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

              - Pressure Rating: [300 psig (2070 kPa) at 225 deg F (107 deg C)] <Insert pressure and temperature>.

              - End Connections: Male threaded or grooved.

              - Lining: Inert and noncorrosive, propylene.

  - ENCASEMENT FOR UNDERGROUND METAL PIPING

Retain this article if corrosion protection is required for underground metal piping.

        - Standard: ASTM A 674 or AWWA C105/A 21.5.

        - Material: Linear low-density polyethylene film manufactured of virgin polyethylene material conforming to the requirements of ASTM D 1248, and a minimum thickness of 0.008-inch thickness or, high-density, cross-laminated polyethylene film manufactured of virgin polyethylene material conforming to the requirements of ASTM D 1248, and a minimum thickness of 0.004-inch.

        - Form: Sheet or, Tube

        - Color: Black or, Natural

        - Install polyethylene encasement for Hubless, Service, and Extra Heavy DWV cast iron pipe and fitting systems in accordance with ASTM A74, X3, and CISPI Handbook.

- EXECUTION

      - EARTH MOVING

        - Comply with requirements for excavating, trenching, and backfilling specified in Section 312000 "Earth Moving."

      - PIPING INSTALLATION

        - Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.

          - Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.

          - Install piping as indicated unless deviations to layout are approved on coordination drawings.

        - Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

        - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.

        - Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

        - Install piping to permit valve servicing.

        - Install piping at indicated slopes.

        - Install piping free of sags and bends.

        - Install fittings for changes in direction and branch connections.

        - Install piping to allow application of insulation.

Retain first paragraph below if piping is required to withstand specific design loads.

        - Install seismic restraints on piping. Comply with requirements for seismic-restraint devices specified in [Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."] [Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."]

        - Make changes in direction for soil and waste drainage and vent piping using appropriate branches, bends, and long-sweep bends.

          - Sanitary tees and short-sweep 1/4 bends may be used on vertical stacks if change in direction of flow is from horizontal to vertical.

          - Use long-turn, double Y-branch and 1/8-bend fittings if two fixtures are installed back to back or side by side with common drain pipe.

            - Straight tees, elbows, and crosses may be used on vent lines.

          - Do not change direction of flow more than 90 degrees.

          - Use proper size of standard increasers and reducers if pipes of different sizes are connected.

            - Reducing size of waste piping in direction of flow is prohibited.

        - Lay buried building waste piping beginning at low point of each system.

          - Install true to grades and alignment indicated, with unbroken continuity of invert. Place hub ends of piping upstream.

          - Install required gaskets according to manufacturer's written instructions for use of lubricants, cements, and other installation requirements.

          - Maintain swab in piping and pull past each joint as completed.

        - Install soil and waste and vent piping at the following minimum slopes unless otherwise indicated:

Revise three subparagraphs below as required by authorities having jurisdiction.

          - Building Sanitary Waste: 2 percent downward in direction of flow for piping NPS 3 (DN 80) and smaller; [1] [2] <Insert number> percent downward in direction of flow for piping NPS 4 (DN 100) and larger.

          - Horizontal Sanitary Waste Piping: [2] <Insert number> percent downward in direction of flow.

          - Vent Piping: [1] <Insert number> percent down toward vertical fixture vent or toward vent stack.

        - Install cast-iron soil piping according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook," Chapter IV, "Installation of Cast Iron Soil Pipe and Fittings."

Retain subparagraph below if piping will be in corrosive soil.

          - Install encasement on underground piping according to ASTM A 674 or AWWA C105/A 21.5.

        - Install steel piping according to applicable plumbing code.

        - Install stainless-steel piping according to ASME A112.3.1 and applicable plumbing code.

        - Install aboveground copper tubing according to CDA's "Copper Tube Handbook."

        - Install aboveground PVC piping according to ASTM D 2665.

        - Install underground PVC piping according to ASTM D 2321.

Retain first paragraph and one or more subparagraphs below if these systems are used on Project.

        - Install engineered soil and waste and vent piping systems as follows:

          - Combination Waste and Vent: Comply with standards of authorities having jurisdiction.

          - Reduced-Size Venting: Comply with standards of authorities having jurisdiction.

Retain first paragraph below if ductile-iron, force-main piping is required.

        - Install underground, ductile-iron, force-main piping according to AWWA C600.

          - Install buried piping inside building between wall and floor penetrations and connection to sanitary sewer piping outside building with restrained joints.

          - Anchor pipe to wall or floor. Install thrust-block supports at vertical and horizontal offsets.

Retain subparagraph below if piping will be in corrosive soil.

          - Install encasement on piping according to ASTM A 674 or AWWA C105/A 21.5.

Retain first paragraph below for copper, force-main tubing.

        - Install underground, copper, force-main tubing according to CDA's "Copper Tube Handbook."

Retain subparagraph below if piping will be in corrosive soil.

          - Install encasement on piping according to ASTM A 674 or AWWA C105/A 21.5.

        - Install force mains at elevations indicated.

        - Plumbing Specialties:

          - Install backwater valves in sanitary waster gravity-flow piping.

            - Comply with requirements for backwater valves specified in Section 221319 "Sanitary Waste Piping Specialties."

          - Install cleanouts at grade and extend to where building sanitary drains connect to building sanitary sewers in sanitary waste gravity-flow piping.

            - Install cleanout fitting with closure plug inside the building in sanitary drainage force-main piping.

            - Comply with requirements for cleanouts specified in Section 221319 "Sanitary Waste Piping Specialties."

          - Install drains in sanitary waste gravity-flow piping.

            - Comply with requirements for drains specified in Section 221319 "Sanitary Waste Piping Specialties."

        - Do not enclose, cover, or put piping into operation until it is inspected and approved by authorities having jurisdiction.

        - Install sleeves for piping penetrations of walls, ceilings, and floors.

          - Comply with requirements for sleeves specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

        - Install sleeve seals for piping penetrations of concrete walls and slabs.

          - Comply with requirements for sleeve seals specified in Section 220517 "Sleeves and Sleeve Seals for Plumbing Piping."

        - Install escutcheons for piping penetrations of walls, ceilings, and floors.

          - Comply with requirements for escutcheons specified in Section 220518 "Escutcheons for Plumbing Piping."

      - JOINT CONSTRUCTION

        - Join hub-and-spigot, cast-iron soil piping with gasket joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for compression joints.

        - Join hub-and-spigot, cast-iron soil piping with calked joints according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for lead-and-oakum calked joints.

        - Join hubless, cast-iron soil piping according to CISPI 310 and CISPI's "Cast Iron Soil Pipe and Fittings Handbook" for hubless-piping coupling joints.

        - Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1.

          - Cut threads full and clean using sharp dies.

          - Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

            - Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

            - Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged.

            - Do not use pipe sections that have cracked or open welds.

        - Join stainless-steel pipe and fittings with gaskets according to ASME A112.3.1.

        - Join copper tube and fittings with soldered joints according to ASTM B 828. Use ASTM B 813, water-flushable, lead-free flux and ASTM B 32, lead-free-alloy solder.

        - Grooved Joints: Cut groove ends of pipe according to AWWA C606. Lubricate and install gasket over ends of pipes or pipe and fitting. Install coupling housing sections, over gasket, with keys seated in piping grooves. Install and tighten housing bolts.

        - Flanged Joints: Align bolt holes. Select appropriate gasket material, size, type, and thickness. Install gasket concentrically positioned. Use suitable lubricants on bolt threads. Torque bolts in cross pattern.

        - Plastic, Nonpressure-Piping, Solvent-Cement Joints: Clean and dry joining surfaces. Join pipe and fittings according to the following:

          - Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.

          - PVC Piping: Join according to ASTM D 2855 and ASTM D 2665 appendixes.

      - SPECIALTY PIPE FITTING INSTALLATION

        - Transition Couplings:

          - Install transition couplings at joints of piping with small differences in ODs.

          - In Waste Drainage Piping: [Unshielded] [Shielded], nonpressure transition couplings.

          - In Aboveground Force Main Piping: Fitting-type transition couplings.

          - In Underground Force Main Piping:

            - NPS 1-1/2 (DN 40) and Smaller: Fitting-type transition couplings.

            - NPS 2 (DN 50) and Larger: Pressure transition couplings.

        - Dielectric Fittings:

          - Install dielectric fittings in piping at connections of dissimilar metal piping and tubing.

          - Dielectric Fittings for [NPS 2 (DN 50)] <Insert pipe size> and Smaller: Use dielectric [nipples] [unions].

          - Dielectric Fittings for [NPS 2-1/2 to NPS 4 (DN 65 to DN 100)] <Insert pipe size range>: Use dielectric [flanges] [flange kits] [nipples].

          - Dielectric Fittings for [NPS 5 (DN 125)] <Insert pipe size> and Larger: Use dielectric flange kits.

      - VALVE INSTALLATION

Retain this article if valves are required.

        - Comply with requirements in Section 220523.12 "Ball Valves for Plumbing Piping," Section 220523.13 "Butterfly Valves for Plumbing Piping," Section 220523.14 "Check Valves for Plumbing Piping," and Section 220523.15 "Gate Valves for Plumbing Piping" for general-duty valve installation requirements.

        - Shutoff Valves:

          - Install shutoff valve on each sewage pump discharge.

          - Install gate or full-port ball valve for piping NPS 2 (DN 50) and smaller.

          - Install gate valve for piping NPS 2-1/2 (DN 65) and larger.

        - Check Valves: Install swing check valve, between pump and shutoff valve, on each sewage pump discharge.

        - Backwater Valves: Install backwater valves in piping subject to backflow.

          - Horizontal Piping: Horizontal backwater valves.[ Use normally closed type unless otherwise indicated.]

          - Floor Drains: Drain outlet backwater valves unless drain has integral backwater valve.

          - Install backwater valves in accessible locations.

          - Comply with requirements for backwater valve specified in Section 221319 "Sanitary Waste Piping Specialties."

      - INSTALLATION OF HANGERS AND SUPPORTS

Retain first paragraph below for projects in areas that require seismic restraints.

        - Comply with requirements for seismic-restraint devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

        - Comply with requirements for pipe hanger and support devices and installation specified in [Section 220529 "Hangers and Supports for Plumbing Piping and Equipment."] [Section 220548.13 "Vibration Controls for Plumbing Piping and Equipment."]

          - Install [carbon-steel] <Insert material> pipe hangers for horizontal piping in noncorrosive environments.

          - Install [stainless-steel] [fiberglass] pipe hangers for horizontal piping in corrosive environments.

          - Install [carbon-steel] <Insert material> pipe support clamps for vertical piping in noncorrosive environments.

          - Install stainless-steel pipe support clamps for vertical piping in corrosive environments.

          - Vertical Piping: MSS Type 8 or Type 42, clamps.

          - Install individual, straight, horizontal piping runs:

            - 100 Feet (30 m) and Less: MSS Type 1, adjustable, steel clevis hangers.

            - Longer Than 100 Feet (30 m): MSS Type 43, adjustable roller hangers.

            - Longer Than 100 Feet (30 m) if Indicated: MSS Type 49, spring cushion rolls.

          - Multiple, Straight, Horizontal Piping Runs 100 Feet (30 m) or Longer: MSS Type 44, pipe rolls. Support pipe rolls on trapeze.

          - Base of Vertical Piping: MSS Type 52, spring hangers.

        - Install hangers for [cast-iron] [steel] [stainless-steel] [and] [copper] soil piping, with maximum horizontal spacing and minimum rod diameters, to comply with MSS-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Install hangers for PVC piping, with maximum horizontal spacing and minimum rod diameters, to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - Support horizontal piping and tubing within 12 inches (300 mm) of each fitting[, valve,] and coupling.

        - Support vertical runs of [cast iron] [steel] [stainless-steel] [and] [copper] soil piping to comply with MSS-58, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

        - All horizontal piping 5” and larger branch openings, or changes in direction shall be suitably restrained to prevent movement of joints and possible separation. Restraints can be field fabricated, or pre-engineered and manufactured.

        - Support vertical runs of PVC piping to comply with manufacturer's written instructions, locally enforced codes, and authorities having jurisdiction requirements, whichever are most stringent.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Drawings indicate general arrangement of piping, fittings, and specialties.

        - Connect soil and waste piping to exterior sanitary sewerage piping. Use transition fitting to join dissimilar piping materials.

        - Connect waste and vent piping to the following:

Revise first four subparagraphs below to suit Project.

          - Plumbing Fixtures: Connect waste piping in sizes indicated, but not smaller than required by plumbing code.

          - Plumbing Fixtures and Equipment: Connect atmospheric vent piping in sizes indicated, but not smaller than required by authorities having jurisdiction.

          - Plumbing Specialties: Connect waste and vent piping in sizes indicated, but not smaller than required by plumbing code.

          - Install test tees (wall cleanouts) in conductors near floor and floor cleanouts with cover flush with floor.

Pit installation option in first subparagraph below should be indicated on Drawings.

          - Install horizontal backwater valves [with cleanout cover flush with floor] [in pit with pit cover flush with floor] <Insert description>.

          - Comply with requirements for [backwater valves] [cleanouts] [and] [drains] specified in Section 221319 "Sanitary Waste Piping Specialties."

          - Equipment: Connect waste piping as indicated.

            - Provide shutoff valve if indicated and union for each connection.

            - Use flanges instead of unions for connections NPS 2-1/2 (DN 65) and larger.

        - Connect force-main piping to the following:

Revise both subparagraphs below to suit Project.

          - Sanitary Sewer: To exterior force main.

          - Sewage Pump: To sewage pump discharge.

        - Where installing piping adjacent to equipment, allow space for service and maintenance of equipment.

        - Make connections according to the following unless otherwise indicated:

          - Install unions, in piping NPS 2 (DN 50) and smaller, adjacent to each valve and at final connection to each piece of equipment.

          - Install flanges, in piping NPS 2-1/2 (DN 65) and larger, adjacent to flanged valves and at final connection to each piece of equipment.

      - IDENTIFICATION

        - Identify exposed sanitary waste and vent piping.

        - Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

      - FIELD QUALITY CONTROL

Portions of testing and inspection requirements in this article are taken from model plumbing codes. Revise if requirements vary.

        - During installation, notify authorities having jurisdiction at least 24 hours before inspection must be made. Perform tests specified below in presence of authorities having jurisdiction.

          - Roughing-in Inspection: Arrange for inspection of piping before concealing or closing-in after roughing-in and before setting fixtures.

          - Final Inspection: Arrange for final inspection by authorities having jurisdiction to observe tests specified below and to ensure compliance with requirements.

        - Reinspection: If authorities having jurisdiction find that piping will not pass test or inspection, make required corrections and arrange for reinspection.

        - Reports: Prepare inspection reports and have them signed by authorities having jurisdiction.

        - Test sanitary waste and vent piping according to procedures of authorities having jurisdiction or, in absence of published procedures, as follows:

          - Test for leaks and defects in new piping and parts of existing piping that have been altered, extended, or repaired.

            - If testing is performed in segments, submit separate report for each test, complete with diagram of portion of piping tested.

          - Leave uncovered and unconcealed new, altered, extended, or replaced waste and vent piping until it has been tested and approved.

            - Expose work that was covered or concealed before it was tested.

          - Roughing-in Plumbing Test Procedure: Test waste and vent piping except outside leaders on completion of roughing-in.

            - Close openings in piping system and fill with water to point of overflow, but not less than 10-foot head of water (30 kPa).

            - From 15 minutes before inspection starts to completion of inspection, water level must not drop.

            - Inspect joints for leaks.

          - Finished Plumbing Test Procedure: After plumbing fixtures have been set and traps filled with water, test connections and prove they are gastight and watertight.

            - Plug vent-stack openings on roof and building drains where they leave building. Introduce air into piping system equal to pressure of 1-inch wg (250 Pa).

            - Use U-tube or manometer inserted in trap of water closet to measure this pressure.

            - Air pressure must remain constant without introducing additional air throughout period of inspection.

            - Inspect plumbing fixture connections for gas and water leaks.

          - Repair leaks and defects with new materials and retest piping, or portion thereof, until satisfactory results are obtained.

          - Prepare reports for tests and required corrective action.

        - Test force-main piping according to procedures of authorities having jurisdiction or, in absence of published procedures, as follows:

          - Leave uncovered and unconcealed new, altered, extended, or replaced force-main piping until it has been tested and approved.

            - Expose work that was covered or concealed before it was tested.

          - Cap and subject piping to static-water pressure of 50 psig (345 kPa) above operating pressure, without exceeding pressure rating of piping system materials.

            - Isolate test source and allow to stand for four hours.

            - Leaks and loss in test pressure constitute defects that must be repaired.

          - Repair leaks and defects with new materials and retest piping, or portion thereof, until satisfactory results are obtained.

          - Prepare reports for tests and required corrective action.

      - CLEANING AND PROTECTION

        - Clean interior of piping. Remove dirt and debris as work progresses.

        - Protect sanitary waste and vent piping during remainder of construction period to avoid clogging with dirt and debris and to prevent damage from traffic and construction work.

        - Place plugs in ends of uncompleted piping at end of day and when work stops.

Consider using other piping or specify protection by shielding or lightweight insulation if piping surface temperatures are expected to exceed 140 deg F (60 deg C).

        - Exposed PVC Piping: Protect plumbing vents exposed to sunlight with two coats of water-based latex paint.

        - Repair damage to adjacent materials caused by waste and vent piping installation.

  - PREVENTIVE MAINTENANCE

- All piping coming from parking deck drains shall be flushed with clean water for not

- less than 10 minutes in each drain after winter season, and every 120 days. If chemicals are used to clean garage walls, this chemical shall be washed off the exterior of the pipe.

- B. 	All piping from dedicated soda station floor sinks shall be flushed by dumping a basin of 5 gallons of warm clean water every 3rd day into the floor sink.

- C.	All piping connected to “low flow” fixtures shall be flushed with clean water by filling, and releasing a utility wash basin sink from the furthest point possible not less than once every 7 days.

- 3.12         PIPING SCHEDULE

- Retain and revise applicable piping applications in this article. Coordinate with materials specified. Revise to suit Project.

        - Flanges and unions may be used on aboveground pressure piping unless otherwise indicated.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Aboveground, soil and waste piping [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be [any of] the following:

Retain one or more of first seven subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

          - Hubless, cast-iron soil pipe and fittings; [CISPI] [heavy-duty] hubless-piping couplings; and coupled joints.

          - Galvanized-steel pipe, drainage fittings, and threaded joints.

          - Stainless-steel pipe and fittings, sealing rings, and gasketed joints.

          - Copper Type DWV tube, copper drainage fittings, and soldered joints.

          - Solid Wall PVC pipe, PVC socket fittings, and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Aboveground, soil and waste piping [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be [any of] the following:

Retain one or more of first five subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

          - Hubless, cast-iron soil pipe and fittings.

          - [CISPI] [heavy-duty] hubless-piping couplings; and coupled joints.

          - Galvanized-steel pipe, drainage fittings, and threaded joints.

          - Stainless-steel pipe and fittings, sealing rings, and gasketed joints.

          - Solid Wall PVC pipe, PVC socket fittings, and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Aboveground, vent piping [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first seven subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

          - Hubless, cast-iron soil pipe and fittings; [CISPI] [heavy-duty] hubless-piping couplings; and coupled joints.

          - Galvanized-steel pipe, drainage fittings, and threaded joints.

          - Stainless-steel pipe and fittings gaskets, and gasketed joints.

          - Copper Type DWV tube, copper drainage fittings, and soldered joints.

            - Option for Vent Piping, NPS 2-1/2 and NPS 3-1/2 (DN 65 and DN 90): Hard copper tube, Type M (Type C); copper pressure fittings; and soldered joints.

          - Solid Wall PVC pipe, PVC socket fittings, and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Aboveground, vent piping [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Service class, cast-iron soil pipe and fittings; gaskets; and gasketed joints.

          - Hubless, cast-iron soil pipe and fittings; [CISPI] [heavy-duty] hubless-piping couplings; and coupled joints.

          - Galvanized-steel pipe, drainage fittings, and threaded joints.

          - Solid Wall PVC pipe, PVC socket fittings, and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Underground, soil, waste, and vent piping [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first five subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - [Extra Heavy] [Service] class, cast-iron soil piping; [gaskets; and gasketed] [calking materials; and calked] joints.

          - Hubless, cast-iron soil pipe and fittings; [CISPI] [heavy-duty] [cast-iron] hubless-piping couplings; and coupled joints.

          - Stainless-steel pipe and fittings, gaskets, and gasketed joints.

          - Solid Wall PVC pipe, PVC socket fittings, and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Underground, soil and waste piping [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first three subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - [Extra Heavy] [Service] class, cast-iron soil piping; [gaskets; and gasketed] [calking materials; and calked] joints.

          - Hubless, cast-iron soil pipe and fittings; [CISPI] [heavy-duty] [cast-iron] hubless-piping couplings; coupled joints.

PVC piping in first subparagraph below is limited to NPS 12 (DN 300).

          - Solid Wall PVC pipe; PVC socket fittings; and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings: [Unshielded] [Shielded], nonpressure transition couplings.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Aboveground sanitary-sewage force mains [NPS 1-1/2 and NPS 2 (DN 40 and DN 50)] <Insert pipe size range> shall be[ any of] the following:

Retain one or both subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Hard copper tube, Type L (Type B); copper pressure fittings; and soldered joints.

          - Galvanized-steel pipe, pressure fittings, and threaded joints.

Retain "any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Aboveground sanitary-sewage force mains [NPS 2-1/2 to NPS 6 (DN 65 to DN 150)] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of three subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Hard copper tube, Type L (Type B); copper pressure fittings; and soldered joints.

          - Galvanized-steel pipe, pressure fittings, and threaded joints.

          - Grooved-end, galvanized-steel pipe; grooved-joint, galvanized-steel-pipe appurtenances; and grooved joints.

Retain " any of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Underground sanitary-sewage force mains [NPS 4 (DN 100) and smaller] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - [Hard] [Soft] copper tube, Type L (Type B); [wrought-]copper pressure fittings; and soldered joints.

          - Ductile-iron, mechanical-joint piping and mechanical joints.

          - Ductile-iron, push-on-joint piping and push-on joints.

          - Ductile-iron, grooved-joint piping and grooved joints.

          - Fitting-type transition coupling for piping smaller than NPS 1-1/2 (DN 40) and pressure transition coupling for NPS 1-1/2 (DN 40) and larger if dissimilar pipe materials.

Retain " any of" option in paragraph below to allow Contractor to select piping materials from those retained.

        - Underground sanitary-sewage force mains [NPS 5 (DN 125) and larger] <Insert pipe size range> shall be[ any of] the following:

Retain one or more of first four subparagraphs below. If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Hard copper tube, Type L (Type B); [wrought-]copper pressure fittings; and soldered joints.

          - Ductile-iron, mechanical-joint piping and mechanical joints.

          - Ductile-iron, push-on-joint piping and push-on joints.

          - Ductile-iron, grooved-joint piping and grooved joints.

          - Pressure transition couplings if dissimilar pipe materials.

END OF SECTION 221316